44.	Grievances. Grievances (If Any) by any Bidder may be sent / addressed to Secretary Federal Board of Intermediate and Secondary Education Islamabad within 07 days after results announcement.

45.	Evaluation Criteria. Criteria will be as per PART-D of this RFP.

46. 	Irrelevant Documents. Any irrelevant document beyond RFP requirement will be considered as negative and may lead to rejection of Bid.

47.	RFP Price and Earnest Money. 	Bidder must enclose in Technical Bid Rs.10000/- as non-refundable RFP price in the form of Demand Draft (DD) and lump sum amount of Rs: 1200000/- (Rupees 1.2 Million only) earnest money in the name of Secretary Federal Board of Intermediate and Secondary Education and such securities should be included in Technical Bid. (Mandatory)

48.Evaluation of Bids. Evaluation will be made as per PART-D of the RFP as per merit. The purchaser is not bound to award contract to lowest bidder.

49. Performance Bond. Successful bidder has to submit 10% of total value as performance guarantee in the form of Bank Guarantee upon signing of contract in case of winning of the bid. Performance Guarantee must be valid for one and half year from the date of signing of contract. It will be released after the first year Energy Performance Evaluation by Consultant.

PART- C: TECHNICAL SPECIFICATIONS/REQUREMENTS

SOLAR PV SYSTEM

Solar PV system of 300KWp to be installed on turnkey basis at FBISE.A complete Single Line Diagram (SLD) from PV Modules to Injection must be given. System must include net metering fulfilling all the requirements of net metering SOPs of local DISCO and NEPRA SRO 892(1)/2015. The system must be complete with protections devices (Earthing, Anti-Islanding, AC/DC Disconnects, Manual Switch, Lightning Arrestors, Surge Protection, AC/DC Current and Voltage Monitoring), solar mounting structure at concrete pads at roof top (civil work for concrete pads 12x1x12 Cubic Inches will be responsibility of the Bidder as per drawing by Bidder), AC Power Distribution Cabinet ( LV Panel) must house all the AC disconnects, Bus bars, Manual ON/OFF switch, fuses, Uni-directional energy meter, Voltage and Current meters etc. System must be capable of monitoring energy data at remote mobile/Laptop/Computer and Purchaser will provide WIFI connection to Inverter. System must be complete with all components and accessories.

SOLAR SYSTEM COMPONENTS

Solar PV Modules

      - Number of Cells and Type= 72 Cells Mono PERC Half Cut Technology

      - Solar PV modules should be Tier-1 type as per BNEF List 2020.

      - Each PV module not less than 540W MONO PERC Half Cut Technology.

      - The modules must have efficiency not less than 20%.

      - Fill Factor not less than 0.78%.

      - Modules must be TUV Rhineland certified as per IEC standards 61215 and 61730 latest edition.

      - Minimum 10 years replacement warranty and 25 years performance warranty

      - Size of total PV modules: Not less than 300KWp at STC but bidders can increase size to achieve Minimum Guaranteed Energy (MGE) of 4KWh/KWp/Day upon completion of first year.

      - Flash Test report and Module Test report as per IEC Standards 61215 and 61730 (Latest Editions) should be provided after delivery.

      - Must be supplied with connected cables and MC4 connectors

      - Preferred brands will be JINKO, LONGI and Trina

      - Annual degradation should not be more than 2% in First year and subsequently 0.55% annually.

Solar On-Grid Inverters

- Minimum individual Inverter size should not be less than100 KW.

- Type of Inverters = Three phase Grid Tied String Inverters

- 5 years warranty from the date of installation

- Make: EUROPE/CHINA (Preferred brands will be Huawei and Sungrow or equivalent)

- Maximum Efficiency: not less than 98%.

- Total Harmonic Distortion: Less than 3%

- Standards compliance: UL 1741, IEC 62109-1/2, IEC 62116, IEC 61683 and IEC 61727

- Degree of protection: Minimum IP 66

- Built-in SPD on DC and AC side.

- Built with Data Logger, Data Dongle, Communication Interfaces Protections, RS232/Ethernet (Network Supported) And Remote Monitoring Capability.

- Smart Meter should be provided to stop energy export till the net metering is made operational.

Solar Mounting Structure

- Mild Steel Hot Dip Galvanized with SS 304 Nuts, Bolts, anchor boltsand Washers to be mounted on concrete pads each of size 12x12x12 Cubic Inches minimum. Gauge should not be less than 12 SWG. Center support of each mounting frame is must and all frames must be connected with each other through a separate Cross channel on the back to avoid any risk of fly over of modules and vibrations/stress in case of wind storms.

- Structure must withstand at 150 KM per hour wind load and harsh environment.

- Nuts, Bolts, Washers, and other supporting accessories must be of stainless steel with appropriate gauges as per design with rust proof capability.

- Drawing of Structure (AutoCAD drawing converted in pdf) showing side, front, and top view with dimensions of each channel and material type, Tilt Angle, SS Nut, boltsand washers must be provided.(Mandatory). PV mounting sketch is not allowed.

- Undersized gauge is not allowed.

- Sagging and material rusting is not allowed.

- The tilt angle of mounting structure must not be less than 26. (Mandatory).

- Windstorms are common phenomena in view of climate changes, so mounting design must withstand harsh environments and free from vibrations and rusting.

- Center support in mounting is must to avoid sagging.

- More than two modules in landscape are not allowed at all in each structure frame and more than one Module in Portrait is not allowed

- L2 (Two modules in landscape setting) or P1 (one module in Portrait setting) both are allowed.

- In case of Aluminum Structure, the gauge of each channel must be double the gauge of MS Hot Dip Channel.

Combiner Boxes

Must be manufactured with GI material with 100% copper strips in it for termination of PV arrays. Must comply with IP 67 and must house fuses/Circuit Breakers.

MC4 Connectors

- Qty: As per design

- Current rating: As per design

- Ingress protection: IP 67

- Standard Compliance: EN 50521:2008

Remote Monitoring At Common Monitoring LED

Whole System must have capability to monitor Power and energy data at minimum 50 Inch Smart LED display of Samsung/SONY Make. Bidders have to supply LED along with any interfacing, hardware/Software required for display of health of the system at LED. Energy parameters displayed must be Load watts, Export to Grid, Energy consumed, PV watts, DC Energy (KWh) and AC KWh injected energy by each system, Total DC and AC KWh, String Monitoring, data graphs, Alarms and patterns etc. LED will act as Dashboard to be installed at suitable visible place.

Civil Work

Civil work for high Quality concrete pads having minimum dimensions of 12x12x12 Cubic Inches will be the responsibility of Bidder as per drawing provided by the Bidder as per Module sizing. Concrete pads quality must be excellent. Concert pads should be placed at 5 inches Nails set of QTY 04 having some penetration in roof to avoid dragging of the Concrete pads in case of hurricanes.

Manuals

The successful Bidder will supply all the service and maintenance manuals in hard and soft copy of each component of the system along with the supply.

System Protections

- System must be complete with all protections including DC and AC Disconnects, DC/AC Surge protection, Lightning arresters and Grounding etc.

- Surge protection shall be provided on the DC side and the AC side of the PV system.

- The Lightning Arresters must be provided and numbers to be designed as per site conditions to avoid any damage because of Lightning.

- A minimum of two separate dedicated copper earth electrodes (DC and AC) connected through a copper wire with the Earthing rods in two pits must be used for the Earthing at DC and AC side of solar PV system (structure, Inverter, SPDs etc.) with a total earth resistance not exceeding 3 ohms at DC and AC Side.

- All metallic Chassis of DC and AC PV Components requiring Earthing must be earthed separately as per net metering SOP of local DISCO.

Net Metering

Solar system must comply with the SRO 892(1) 2015 and DISCO SOP for net metering. Bidder will process the net metering license as per DISCO SOPs and NEPRA SRO during the installation to save time. Bidder should include all expenses for net metering as integral part of Bid. Bidder must have net metering permission License from AEDB. Smart Meter must be installed with system on operation for zero export of extra energy to Grid till the net metering will be active.

PV DC Cables

- Single core 99.9% copper cable with conductor withstanding at temperature of 120 Degree maximum.

- Cables must be double insulated tested at 1.5 KV.

- Weather resistant, UV resistant, Ozone corrosion resistant, halogen free and flame resistant.

- XLPE/XLPO Insulation withstanding temperature range from -4-degree C to 120 Degree C.

- Cable must be tested as per Solar PV standard IEC 51608 or IEC 62930 and test report must be provided along with Type Tested certificate.

- In case of cable from Local manufacturer, the warranty must be minimum five years at Manufacturer’s letter head and compliance as IEC 50618/62930 Must be assured.

AC Power Distribution/LV Cabinet

AC Power Distribution Cabinet (LV Cabinet) must contain AC circuit breakers, contactors, bus bars, KWh energy meter, AC SPD and OFF/ON main switch with monitoring of Voltage, current, Power and, Energy. The components must of high-quality complying with national standards of switchgears.

Preferred brands are Tariq Electric, Technob Engineering, Southern Electric Asian Concern, Bilal Switchgear Engineering, MK Engineering or any reputed Quality switchgear manufacturer.

Injection of Energy

Energy will be injected at 440V Existing Distribution panel available, but the Bidder has to supply separate AC Power distribution cabinet (LV cabinet) with built-in protection, automatic and manual isolation from the distribution circuit.

Technical Datasheets

Technical datasheet of each PV component must be provided in technical Bid. (Mandatory).

PV DIESEL SYSTEM CONTROLLER/SYNCHRONIZER

PV DIESEL Synchronizer/controller should provide harmony and smooth operation of PV with Diesel GenSet providing intelligent control mechanism for joint operation of PV and Diesel set with the objective of optimum and reliable power to the load. It must guarantee a constant power balance (reactive and active) within a PV GENSET system at all times. ATS is already Present with GenSet for auto-start of diesel generator. Diesel Generator set of 400 KVA is already available.

General Engineering Work

The cable laying ducts/Channels from PV Modules to Inverters must be of MS Hot dip with no possibility of entering of any sects or animals and all internal cable laying channels/ducts connecting the Inverters, Ducting and cable laying must be of perforated MS Galvanized/Slotted high quality PVC duct. Interconnection of PV modules must be through MC4 cables/connectors without any joint and MC4 cables interconnecting PV Modules must not be very tight and should have some play to avoid cable cracking. All concrete pads must be high quality martial mix and must be at same level so that the structure should not look as curved or raised at some point. Earthing material and work should be of high quality. Earthing required is at DC and AC with two separate bores. The structure must be vibration and rust free and must withstand harsh environments. The workmanship should be high quality through trained and experienced technicians and engineers. All thimbles and connectors must be of high quality.

PART D- EVALUATION OF BIDS

Final bid evaluation shall be carried on quality cost method with 60%:40% weightage for Technical and Financial bid respectively.

Bids shall be technically evaluated first as per the following technical evaluation criteria. One part is mandatory without which the bids will be rejected without further evaluation. Second part is numbered evaluation and passing marks are 60%

| Sr. | Evaluation Parameters | Status | YES/NO |  | Remarks if any |
| --- | --- | --- | --- | --- | --- |
| A - MANDATORY ITEMS – NON-NUMBERED * |  |  |  |  |  |
| 1 | COMPLETE BOQ as per FORM D | Yes/No | - |  |  |
| 2 | SYSTEM DESIGNED AS PER RFP | YES/NO | - |  |  |
| 3 | SYSTEM DESIGN REPORT WITH year wise INJECTED AC ENERGY with minimum 4 KWh/KWp/Day in first year | YES/NO | - |  |  |
| 4 | DATASHEETS AS PER SPECIFCATIONS(Clearly readable) * | YES/NO | - |  |  |
| 5 | Five years warranty of whole system with free material and labor at bidder’s letter head. | Yes/No | - |  |  |
| 6 | Valid Income. Tax & Sales Tax Registration Certificates | Yes/No | - |  |  |
| 7 | Earnest Money attached. | Yes/No | - |  |  |
| 8 | Provision of Non Black Listing record on company letter head duly signed and stamped on company letter head* | Yes/No | - |  |  |
| 9 | PEC and AEDB Certificates | Yes/No | - |  |  |
| 10 | Duly filled and stamped FORM A, B, C and D | YES/NO |  |  |  |
| 11 | PV Cable test report from accredited LAB as per IEC 50618 or 92930. | Yes/NO |  |  |  |
| BIDS WILL BE DISQUALIFIED IF ANY OF ABOVE ITEM IS MARKED “NO” |  |  |  |  |  |
| B | MANDATORY – NUMBERED ITEMS | Obtained | Total |  |  |
| 1 | Solar PV Module TIER-1 with Complete test report as per IEC 61215 and 61730 (Latest Edition) |  | 20 | 20 Number for TIER-1 with complete Test report and zero for others |  |
| 2 | INVERTER as per preference with IEC certificates mentioned in PART C of RFP. |  | 20 | 20 Number for Inverter with Test reports and zero for others |  |
| 3 | NUMBER OF THREEGRADUATE ENGINEERS WITH VALID PEC CARD HAVING MORE THAN THREE YEARS EXPERIENCE |  | 10 | 10 for Five Graduate Engineers with three years’ experience and 05 for less experience |  |
| 4 | Clearly Readable Technical Datasheets of each component provided as per BOQ |  | 10 | 10 for complete and 0 for incomplete literature. |  |
| 5 | 100KWp Solar On-grid Projects Completed successfully with attached Performance certificates |  | 10 | 10 for three Projects and zero for others. |  |
| 6 | PEC and AEDB Certificate |  | 10 | 10 for certified and zero for non-certified |  |
| 7 | Company Experience from the date of its incorporation |  | 10 | 10 for 03 years ad zero or others |  |
| 8 | Last Month Bank Statement having closing balance of more than 40 million |  | 10 | 10 for Rs.10 M balance and five for others |  |
| Total Technical Marks |  | - | 100 |  |  |
| Minimum Technical Qualification Marks |  |  | 60 |  |  |
| Marks Obtained |  |  |  |  |  |

PART E - FORMS TO BE SUBMITTED

FORM-A

At Bidder Letter Head

BID SUBMISSION UNDERTAKING

Secretary

Federal Board of Intermediate and secondary Education

H-8/4, Islamabad

Karachi.

Dear Sir

1.	We, the undersigned, offer to provide our system with services for “300KWp rooftop On-grid Solar PV System on Turnkey basis” in accordance with your RFP Document Number FBISE SOLAR / 300KWp dated -----------------, 2022.

We are hereby submitting our Bid, which includes technical as well as financial Bid as per instructions.

2.	We hereby acknowledge and agree to all terms, conditions, special provisions, and instructions included in the above-referenced RFP document.

3.	We understand and agree that the decision of the procurement / evaluating committee shall be final and cannot be challenged on any ground at any forum and the procurement / evaluating committee will not be liable for any loss or damage to any party acting in reliance thereon.

4.	Furthermore, we hereby certify that, to the best of our knowledge and belief: -

a.	We have no close, financial or familial relationships with any Askari-V staff members.

b.	We have no close, financial or familial relationships with any other Bidder	submitting Bids in response to the above-referred RFP document.

c.	The prices in our offer have been arrived independently, without any consultation, 	communication, or agreement with any other Bidder or competitor for the purpose 	of restricting competition.

d.	All information in our Bid and all supporting documentation are authentic and 	accurate.

e.	We understand and agree to FBISE prohibitions against fraud, bribery, and kickbacks.

5.	We hereby certify that the enclosed representations, certifications, and all other submitted documents / statements are accurate, current, and complete.

Authorized Signature and stamp

M/s (Bidder’s Name)

Dated

------------------------------------------------------------------------------------------------------------------------------

FORM –B

LIST OF 100KWp and above On-grid Solar PV projects Completed in Pakistan

Mandatory for Last 03YEARS

| Name of Project | Client Name | Contact Nr (Cell and Landline) | Client Complete Address | Date of Completion |
| --- | --- | --- | --- | --- |

NOTE: No project other than PV Plant of less than 100KWp

FORM -C(TECHNICAL BOQ)

(ToBe Included In Technical Bid)

TECHNICAL BOQ FOR 300KWp Solar PV On-Grid System

| Component Name | RATING/Specifications | QTY (Nr / Set/Job) | Manufacturer Name/Supplier Name | Brand/Model | Country of Origin | Local/Imported | Warranty as per RFP |
| --- | --- | --- | --- | --- | --- | --- | --- |
| PV Modules | ------------Wp Tire-1 PV Module Mono PERC Half Cut | ------ |  |  |  |  | 10 years replacement and 25 years performance |
| Three Phase PV Inverter | -------------KW On-grid with Wi-FiDonggle | 01 |  |  |  |  | Five Years warranty |
| Data logger | ---------------- | 01 |  |  |  |  |  |
| PV Cables | Single core PV Cable------mm as per IEC 50618/62930 | As per System |  |  |  |  | Five years warranty in case of Local |
| PV Mounting structure | Hot Dip 12 Guage mounting structure with SS Nuts and Bolts | As per System |  |  |  |  | 10 years warranty |
| AC Cables | Four Core----------mm cable | As per system |  |  |  |  | Five Years warranty |
| Earthing Package including boring, cables and material | As per DISCO/NEPRA SRO 892/2015 as per RFP | 01 Job |  |  |  |  | Five years warranty |
| Power Distribution Cabinet (LV Cabinet) | MS powder coated Panel having bus bars, circuit breakers, disconnects, manual switch, Energy Meter etc. | 01 |  |  |  |  | Five years warranty |
| Lightening Arrestors | Copper lightening arrestor for radius coverage of -------------meter with ----------spikes. | 03 |  |  |  |  | Five years warranty |
| Net Meter | NTDC/IESCO Approved Net Meter | 01 |  |  |  |  | Five years warranty |
| Outside Main Disconnect | 440V/----A AC disconnect switch | 01 |  |  |  |  | Five years warranty |
| PV GenSet Synchronization | PV Diesel GenSet Synchronization system including controller, switching, cabling and Interfaces | 01 set |  |  |  |  | Five Years warranty |
| Services | Design, Supply, installation, commissioning, Testing & Net metering | 01 Job |  |  |  |  | Five Years Warranty |

Turnkey System is complete with Civil, Mechanical, Electrical work, Net Metering and training of client persons.

Notes: Two brands one primary and one alternate are allowed only for Solar Modules and one brand for all other items, and word Equivalent is not allowed (Mandatory)

Where manufacturer is not available, write supplier name and do not leave any cell empty.

FORM -D(FINANCIAL BID)

(To Be Included In Financial Bid at Bidder’s Letterhead)

PRICE FOR 300 KWp Solar PV On-Grid System

| Component Name | RATING/Specifications |  | QTY (Nr / Set/Job) | Manufacturer Name/Supplier Name | Brand/Model | Country of Origin | Local/Imported | Warranty as per RFP |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| PV Modules | ------------Wp Tire-1 PV Module Mono PERC Half Cut |  | ------ |  |  |  |  | 10 years replacement and 25 years performance |
| Three Phase PV Inverter | -------------KW On-grid with Wi-FiDonggle |  | 01 |  |  |  |  | Five Years warranty |
| Data logger | ---------------- |  | 01 |  |  |  |  |  |
| PV Cables | Single core PV Cable------mm as per IEC 50618/62930 |  | As per System |  |  |  |  | Five years warranty in case of Local |
| PV Mounting structure | Hot Dip 12 Guage mounting structure with SS Nuts and Bolts |  | As per System |  |  |  |  | 10 years warranty |
| AC Cables | Four Core----------mm cable |  | As per system |  |  |  |  | Five Years warranty |
| Earthing Package including boring, cables and material | As per DISCO/NEPRA SRO 892/2015 as per RFP |  | 01 Job |  |  |  |  | Five years warranty |
| Power Distribution Cabinet (LV Cabinet) | MS powder coated Panel having bus bars, circuit breakers, disconnects, manual switch, Energy Meter etc. |  | 01 |  |  |  |  | Five years warranty |
| Lightening Arrestors | Copper lightening arrestor for radius coverage of -------------meter with ----------spikes. |  | 03 |  |  |  |  | Five years warranty |
| Net Meter | NTDC/IESCO Approved Net Meter |  | 01 |  |  |  |  | Five years warranty |
| Outside Main Disconnect | 440V/----A AC disconnect switch |  | 01 |  |  |  |  | Five years warranty |
| PV GenSet Synchronization |  | PV Diesel GenSet Synchronization system including controller, switching, cabling and Interfaces | 01 set |  |  |  |  | Five Years warranty |
| Services | Survey, Design, Supply, installation, commissioning, Testing and Net metering |  | 01 Job |  |  |  |  | Five Years Warranty |
| TURNKEY PRICE FOR 300 KWp Solar ON-Grid System = US Dollar .-------------- In words: --------------------------------------------------------------------- |  |  |  |  |  |  |  |  |

Turnkey System is complete with Civil, Mechanical, Electrical work, Net Metering and Training of Client Persons.

Notes:

- Submit Price is US Dollar and it will be converted into PAK Rupees as per Bank Exchange rate at the time of the contract.

- Two brands one primary and one alternate are allowed only for Solar Modules and one brand for all other items, and word Equivalent is not allowed.(Mandatory)

- Where manufacturer Name is not available write supplier name and do not leave any cell empty.

Signed and stamped.

---------------------------------------------------------------------------------END------------------------------------------------------------------------------------------------